## Sheet1
UPS Sizing
Single System (2 ch) avg power consumption
Load | Avg Power (W) | Qty of loads | Total power from load (W) | Load power factor | Total power from load (VA)
Heater | 20 | 1 | 20 | 0.98 | 20.4082
Fan | 10 | 2 | 20 | 0.8 | 25
Batt Charge | 30 | 2 | 60 | 0.98 | 61.2245
5V PSU | 10 | 1 | 10 | 0.56 | 17.8571
|  | Total Load (W) | 110 | Total Load (VA) | 124.4898
Total System Load
Battery Cycler Units(2 ch) | 110 | 6 | 660 |  | 746.9388
usb hub | 10 | 1 | 10 | 0.5 | 20
DAQ computer | 300 | 1 | 150 | 0.8 | 187.5
|  | Toal Load(W) | 820 | Total Load (VA) | 954.4388

## Sheet2
UPS COSTS
Non-Rack mount
Unit cost | Rated load (W) | Cost per watt | run time (min) | energy (Wh) | Cost per Wh | unit
139.64 | 540 | 0.25859 | 5 | 45 | 3.1031 | APC RS 800VA
281.29 | 600 | 0.46882 | 7.4 | 74 | 3.8012 | APC SC1000VA
346.12 | 865 | 0.40014 | 7.6 | 109.5667 | 3.159 | APC SC1500VA
508.72 | 980 | 0.5191 | 6.7 | 109.4333 | 4.6487 | APC smart UPS 1500 usb
Rack mount
unit cost | rated load | cost / watt | run time | energy (Wh) | cost per Wh | unit
171.56 | 280 | 0.61271 | 5.9 | 27.5333 | 6.231 | SC 450VA
408.97 | 480 | 0.85202 | 5.5 | 44 | 9.2948 | APC Spart UPS 750VA
514.99 | 800 | 0.64374 | 8.1 | 108 | 4.7684 | APC Smart-UPS x 1000
651.36 | 980 | 0.66465 | 7.4 | 120.8667 | 5.3891 | APC Smart-UPS 1500VA
1050.36 | 1980 | 0.53048 | 5.2 | 171.6 | 6.121 | APC Smart-UPS 2200VA